## Leakage
| Sub Component | APR18 Comp R/A/G | APR18 Element R/A/G | Cause for red/amber status | Outline plan to turn it green March 2019 | Expected compliance date | Expectation for APR19
1 | Coverage
1a | 95% of all properties have continuous night flow monitoring through the year
2 | Availability
2a | At least 90% of all properties within continuous night flow monitoring networks available for reporting night flow data through the year |  |  | There are a range of issues affecting availability of DMAs including meter faults, configuration issues, PCC out of range etc. Detailed investigations are ongoing so that plans can be put in place to improve. Transition from Netbase 5 to Netbase 6 will allow greater flexibility to understand structural or data issues within DMAs. | Transition to NB6 is onging as DMAs continue to be validated - configuration/ asset data issues. Due to complete April 2019. Likely to require follow up ALC sweeps/ data improvement activities (meter, valve, configuration checks). Will need to be planned in with other Ops activity. | 2019-10-01
3 | Properties
3a | All properties mapped to defined zones or DMAs using geo-location or similar methods |  |  | There is currently no individual property geo-location. Property postcode from the billing system has been mapped to DMA boundary in Netbase. This historical process is not able to be verified but there are discrepancies with property seed data held in the company GIS system. Current transition activities include migration of GIS data to STW GISST and creation of asset data in accordance with STW asset standards (property CWDP points allocated to pipes & pipes allocated to DMAs). Also, regular frequent updates to Netbase 6 from billing data & GISST. | Resolved by DVW migration to SVT version of Netbase 6 and GISST. DMA validation exercise due to complete April 2019. Likely to require follow up ALC/ data improvement activities. | 2019-10-01
3b | Consistency of property numbers contained within DMAs or zones with company billing system. Valid differences explained |  |  |  | Resolved by DVW migration to SVT version of Netbase 6 and GISST. DMA validation exercise due to complete April 2019. Likely to require follow up ALC/ data improvement activities. | 2019-10-01
3c | Properties that are defined as void excluded from night use allowances unless evidence for use or losses from illegal occupation is available
3d | Leakage allowance applied for properties not within DMAs or monitored zones consistent with other leakage estimates
3e | Leakage allowance applied for properties not within DMAs or monitored zones consistent with other leakage estimates
4 | Night flow period and analysis
4a | Night flow data frequency at least every 15 minutes
4b | Leakage derived from a fixed period during the night of at least a one hour period and up to two hours
4c | If the fixed period is varied during the year for some or all DMAs or zones to address significant changes to night use patterns such as during Ramadan evidence for this is provided.
4d | Leakage allowance applied for properties not within DMAs or monitored zones consistent with other leakage estimates
4e | Data infilling for a single DMA or zone does not use more than six months of historic data before moving to area average
4f | Data infilling where historic data is not available uses the area average in which the DMA is located
4g | When a DMA is restored to operability, the subsequent leakage data is used to retrospectively update the data infilling interpolating between pre- and post- data over at least one month |  |  | Current version of Netbase system does not have compliant functionality. Able to report compliance in Shadow Netbase database. | Technology project to upgrade to latest version of Netbase. Go Live expected Dec 2019 for parallel running and testing until March 2020 | 2019-12-01
4h | Where NHH properties are continuously monitored, the actual values of flow over the night flow period are used in place of estimates within the night flow analysis
4i | Weekly leakage estimates are used for annual reporting with no exclusions for summer months
4j | Negative leakage values are used in compiling values of annual average leakage
4k | The reasons for any prolonged periods of negative leakage are investigated and explained. |  |  | Periods of negative leakage are not currently investigated. However, we believe these to be minimal and not material to reported leakage. We will include in our new Operating Model the investigation of negative leakage periods. | Negative leakage DMAs will be investigated by operational teams in year 5. Programme will continue through 2019. This will involve data validation exercise to resolve such things as meter/telemetry errors, configuration changes, valve operations. Once data issues resolved and DMA is reporting 'positive' leakage, ALC sweeps will commence. | 2020-03-01
5 | Household night use |  |  | Household night use is set at 1.7 litres per property per hour. It is a single value for the whole company. The value is not updated. | Review of ST and HD demographic representation shows that current ST night use monitors are not representative of the HD region. We plan to establish new monitoring in Wrexham and Powys utilising DMAs. This will require replacement meters and high spec loggers in order to collect the data required to derive night use. This activity will be iundertaken in year 5 with reporting changes expected to be made from start of AMP7 | 2020-03-01
5a | The time period for HHNU is the same time period as used for night flow and NHHNU. |  |  |  | Will be delivered as part of establishing new monitoring as 5.0 above.
5b | Own data or shared data with Proximate companies is used for HHNU. |  |  |  | Will be delivered as part of establishing new monitoring as 5.0 above.
5c | Plumbing losses are included and based on own data |  |  |  | Will be delivered as part of establishing new monitoring as 5.0 above.
5d | Evidence that survey is representative (based on demography, property type or other factors) of the company as a whole |  |  |  | Will be delivered as part of establishing new monitoring as 5.0 above.
5e | Sample size is sufficient to capture continuous and intermittent night use with reasonable confidence |  |  |  | Will be delivered as part of establishing new monitoring as 5.0 above.
5f | Continual monitoring and maintenance of IHM and SAMs monitors |  |  |  | Will be delivered as part of establishing new monitoring as 5.0 above.
5g | HHNU is derived daily with regular, adjustment of values on a weekly or monthly frequency to reflect actual seasonal use. This may be done retrospectively |  |  |  | Will be delivered as part of establishing new monitoring as 5.0 above.
6 | Non household night use |  |  | UKWIR best practice methodologies previously used in the development of Non Household Night Use estimates. However, it has not been possible to validate the precise details of the statistical modelling. | A new non-household model will be used. This is based on the UKWIR principles, with some improvements to avoid the widely accepted calculation errors now in the UKWIR best practice report. This will involve additional logging flow of commercial props in HD. Currently only largest users are continuously logged. A representative sample of all users types will be required. Logging activity will be undertaken throughout 2019, with night use coefficients produced in Q3 2019. Reporting new night use estimates from April 2020 | 2020-03-01
6a | The time period for NHHNU is the same time period as used for night flow and HHNU
6b | Own data or shared data with proximate companies is used for NHHNU
6c | 1999 UKWIR methodology with the appropriate time window as used for the night flow and the published outcome of further methodology development is applied
6d | Stratification of non-households to a number of groups and consumption bands is representative of the varying characteristics of commercial and industrial properties
6e | Sample size is sufficient to capture night use by stratification with reasonable confidence
6f | Reliable and representative average billed volume (ABV) model based on data logging of the Representative sample sufficient to capture demand variations with further seasonal logging where relevant. Continuously logged properties not part of the sample.
6g | ABV model linked to billing system or Replacement database of billed volumes. Average billed volumes updated at least annually
6h | Continuous monitoring of selected non households is carried out where average demand of an individual non household has a material impact on the ability for a DMA or zone to provide valid and consistent data within operability limits
7 | Hour to day conversion |  |  | Hour to Day factors have been calculated for each DMA based on intermittent pressure logging or model data. There has not been a review or recalculation of HDF for some time. | DMA pressure logger installs will be complete by April 2019. An assessment and recalculation of HDFs at DMA level will then take place. These values will be loaded into Netbase for DMA leakage calculations. | 2019-07-01
7a | The hour-to-day factor is derived separately for each DMA or zone using pressure logging within each DMA or zone. The factors are updated at least annually or where there are any significant changes to pressure regimes |  |  |  | Will be delivered as part of the new HDF assessment above
7b | As an alternative, hydraulic models reflecting latest network configuration and pressure changes, are used if they disaggregate in sufficient detail at sub-zone level |  |  |  | Not required once new logging rolled out and HDF assessment complete.
7c | Evidence based N1 value used. Expected range is 1.0 to 1.20 |  |  |  | Will be delivered as part of the new HDF assessment above
8 | Annual distribution leakage
8a | Average weekly data is derived from valid daily values of leakage using data points which are representative of the week. Backfilling using the methods described in Section 5.4 – night flow analysis – is done when valid data is not available for three or more data points.
8b | The annual value of leakage expressed as Ml/d is be derived from an average of the 52 week data.
9 | Trunk main losses (only applicable if DMA level leakage assessment used)
9a | Company-specific data is used to assess the value of trunk main leakage
9b | reactive leakage monitoring approach applied where trunk main losses form a significant element of total leakage or the MLE water balance gap is greater than +/-2%.
9c | If trunk main losses greater than 5% of total leakage estimates reviewed annually
10 | Service reservoir losses (only applicable if DMA level leakage assessment used)
10a | Company-specific data is used to assess the value of service reservoir losses;
10b | Reservoirs with known high leakage, structural deficiencies or at risk of water quality failures are investigated on an individual basis
10c | Drop tests (12 hour duration depending on size) carried out every five or ten years. All valves checked for tight close; and losses through overflows investigated. Appropriate monitoring arrangements in place to control and minimise overflow events.
11 | Distribution input
11a | Distribution input to the system is metered with at least daily readings at all defined locations
11b | Meters are appropriate size for the flow to be measured and located at appropriate inputs to the network confirmed by record plans. Any treatment works take-off downstream of a meter are excluded from the DI calculations
11c | Data validity checks are carried out at least monthly
11d | Missing data is infilled using both pre- and post- data for the location over at least one month, extrapolated from pump hours or use of upstream or downstream meters |  |  | Data is reviewed monthly to identify anomalies. If trends suggest inaccurate data reads or inoperable meters then data is omitted/ infilled to get annual figure. | Current approach is compliant. Will update at APR 19 | 2019-04-01
11e | The data transfer systems from meter output to central database are checked and validated on a risk based frequency from one up to two years |  |  | Manual data transfer system to get daily reads from telemetry outstations (scada) into centrally stored ‘shared’ spreadsheet. | Current approach is compliant. Will update at APR 19 | 2019-04-01
11f | Flow checks are carried out on DI meters consistent with the principles of the document ‘EA Abstraction Good Metering Guide’ and in particular the frequency of flow checking defined in Table 6.2 of the EA guide |  |  | Flow checks are carried out on DI meters, wherever physically possible, when data suggests it is required. It is not possible to carry out flow checks consistent with all the principles of the ‘EA Abstraction Good Practice Guide’ at all DI flow sites. | We are reviewing all DI meters in HD to assess the practicality of verifying all meters. All major works flow meters have been verified in 2018. We will continue to assess and verifiy remaining meters in 2019.
12 | Measured consumption
12a | Metered data is derived from own billing system or from CMOS for non-households
12b | Estimate of supply pipe losses is included for internally metered properties consistent with own current assumption of supply pipe losses
12c | Inclusion of any leakage allowance is included where a rebate has been applied to a customer’s bill |  |  | No leakage allowance is applied to measured consumption data. | Resolved as part of migration to STWs billing system and processes | 2019-04-01
|  |  |  | As part of the transition to STW billing systems, this measure will become compliant. | Resolved as part of migration to STWs billing system and processes | 2019-04-01
12d | Meter under registration is applied consistent with own estimates. Evidence of MUR available especially for MUR above 3%. |  |  | MUR is 3%. Company specific investigations were carried out but results were not conclusive and so an industry average has been chosen. As part of the transition to STW systems, we will adopt their compliant approach to MUR. | Meter under-registration study will involve a desktop study if details of meter type and age are known. If known, an estimate of MUR can be derived from industry data. If not known a sample of meter testing will be required. | 2019-10-01
12e | Meter replacement consistent with own replacement programme
13 | Unmeasured consumption |  |  |  | Review of ST and HD demographic representation shows that current ST monitors are not representative of the HD region. We plan to establish new monitoring in Wrexham and Powys utilising DMAs. This will require replacement meters and high spec loggers in order to collect the data required to derive unmeasured PCC. This activity will be iundertaken in year 5 with reporting changes expected to be made from start of AMP7 | 2020-03-01
13a | Monitors follow principles set out in the UKWIR Report ‘Best Practice for unmeasured per capita consumption monitors 1999’ and the more recent report ‘Future Estimation of Unmeasured Household Consumption’, UKWIR 2017 |  |  | Company specific Individual Household Monitor was in use until a review in 2017. This monitor was set up in line with best practice principles. In 2017, the decision was made to freeze the Unmeasured HH consumption values based on an average of the previous 5 years of data. In order to become compliant DVW will start to move to the STW model of SAMs for deriving unmeasured consumption. We will complete an assessment in 2018 of the two regions customer demographics to understand overall ST and DV representation. This will outline what further SAMs are required. An alternative solution may be to use DMA level monitoring, rather than SAMs to derive PCC. | Review of ST and HD demographic representation shows that current ST monitors are not representative of the HD region. We plan to establish new monitoring in Wrexham and Powys utilising DMAs. This will require replacement meters and high spec loggers in order to collect the data required to derive unmeasured PCC. This activity will be iundertaken in year 5 with reporting changes expected to be made from start of AMP7 | 2020-03-01
13b | Consumption is derived from own individual household monitor or small area surveys
13c | Evidence that survey is representative (based on demography, property type or other factors) of the company as a whole; Valid data available from at least 80% of monitors as an annual average measure. |  |  | The Individual Household Monitor sample is no longer in use. | Will be delivered as part of establishing new monitoring as 13a above.
13d | For companies using SAMs – SAM comprises a representative sample of customer’ characteristics. The sample size is sufficient to provide a statistically representative sample after allowing for outages. Where the proportion of metered properties in an area exceeds 50% of total properties then further data validity tests are applied For companies using IHMs – IHM comprises representative sample of customer characteristics. The sample is at least 1000 properties. |  |  |  | Will be delivered as part of establishing new monitoring as 13a above.
13e | Uncertainty allocated to unmeasured household consumption is estimated and justified |  |  | As part of the transition to STW systems, we will adopt a compliant approach. | Will be delivered as part of establishing new monitoring as 13a above.
13f | There is continual monitoring and maintenance of IHMs and SAM monitors |  |  |  | Will be delivered as part of establishing new monitoring as 13a above.
13g | Meters are selected to provide sufficient granularity to detect low continuous flows indicative of plumbing losses or leakage short duration flow variations. The value of meter under registration is less than the company’s average meter stock |  |  |  | Will be delivered as part of establishing new monitoring as 13a above.
13h | Estimate of plumbing losses is based on own data |  |  |  | Will be delivered as part of establishing new monitoring as 13a above.
13i | Where unmeasured non-household reported volume is less than 2% of total non-household demand, data from a per property consumption study is refreshed every five years |  |  |  | Will be delivered as part of establishing new monitoring as 13a above.
13j | Where unmeasured non-household reported volumes are greater than 2% of non-household demand, data from a property study is refreshed every two years |  |  |  | Will be delivered as part of establishing new monitoring as 13a above.
14 | Company own water use
14a | All sewage treatment sites and other sites and assets supplied downstream of the DI meters using greater than 10 m3/d (0.01 Ml/d) are metered
14b | An estimate of total company own use is included in the water balance, based on a clear methodology and actual data
14c | Estimate of distribution operational use is evidence based and not greater than 0.6% of distribution input. |  |  | Distribution operational use is based on estimated flow rates and timed durations. The current values are an estimate based on historic data. | We will update the approach used in previous years using company specific data for activities: mains flushing, cleaning; reservoir cleaning; standpipe use. | 2020-03-01
15 | Other water use
15a | Other use components are based on own data
15b | Estimate of water delivered unbilled (legally and illegally) is evidence based and not greater than 1.8% of distribution input.
15c | Estimates are updated when there is a material increase or decrease to volumes.
16 | Water balance and MLE
16a | Fully measured components have a range from 2% to 4%
16b | Mainly measured with some estimated adjustments have a range from 2.5% to 5%
16c | Estimated using detailed and reliable methods have a range from 8% to 12%
16d | Broad estimates not fully detailed or reliable have a range from 20% to 50%
16e | Water balance discrepancy <2% = G >2% and <3% = A >3% = R

## Unplanned outage
Dee Valley Unplanned Outage - Gap Analysis
Components taken from Annex A to the Ofwat Reporting Guidance for Unplanned Outage
| Component | Compliant (RAG) | Progress and reason for any non-compliant components | Confidence Grade
1 | PWPC
1a | Annual Review |  | Annual review timed with the half year audit for the following year to review changes. See process described in PDT
1c | PWPC by production site |  | Annual flows reviewed covering period 1 April 18 - 31 Aug 18
1d | Water Resource Zone PWPC |  | PWPC can be aggregated to align with the new zones which will be used in the fWRMP and align to the national boundary. There are 4 zones but two are bulk supplies so only need to do unplanned outage on the two where HD assets supply the water - Wrexham and Llandinam/ Llanwrin.
2 | Asset failure / unplanned outage
2a | Source Data |  | Capacity data defined for all 5 sites, but failure data not yet extracted from systems. Process is outlined in PDT.
3 | Planned outages
3a | Source Data - programme of works |  | Data not fully compliant with new criteria, specific gaps with groundwater data, but mitigated by the fact that its only two sites and gaps can be filled using manual records. Interogation of data delayed due to the company IT integration process and lack of telemetry for remote assets. Action plan in place to address by mid April.
4 | Duration
4a | Start Time |  | process defined, data currently being extracted
4b | End Time |  | process defined, data currently being extracted
4c | Rounding |  | Rounding rules added to the spreadsheet
Reduction in capacity
a | Reduced Capacity |  | Capacity rules set for 5 sites, final review pending.
b | Total Outage |  | Calculation set up in the spreadsheet and validation checks also defined.
5 | Exclusions
| Normal water quality operating band |  | Data available but unable to process data in accordance with rules until outage data is available.
| Evidence of WQ Events |  | Data available for surface water, but not groundwaters (but manual records available for GW sites and being extracted).

## 1 in 50 storm
Hafren Dyfrdwy: Risk of sewer flooding in a 1 in 50 year storm - Gap Analysis
References are made to the reporting guidelines which refer directly to the methodology outlined in "Developing and Trialling Wastewater Resilience Metrics - Final Report for Water UK (7 November 2017)"
| Component | Compliant (RAG) | Progress and reason for any non-compliant components | Confidence Grade
1 | General interpretation of the reporting methodology
1a | Interpretation of the reporting requirements |  | The Ofwat definition (https://www.ofwat.gov.uk/outcomes-definitions-pr19/ - item 10) refers directly to the report "Developing and Trialling Wastewater Resilience Metrics - Final Report for Water UK (7 November 2017)". This report builds on and discusses options on how to build on Ofwat's proposed metric outlined in Appendix 3 of their July 2017 consultation document. Throughout the methodology there is subjectivity and reference to application of engineering judgment and whilst our interpretation of its content is considered a pragmatic and reasonable approach the lack of consistency in this metric will result in variability of reporting across the industry. Notwithstanding this our approach and application of the methodology is considered to be compliant with the reporting components set out in the ""Developing and Trialling Wastewater Resilience Metrics" albeit that other companies may have interpreted it is different ways, yet still be compliant due to the subjectivity of the methodology. Compliance has been flagged as AMBER on the basis that the methodology is too subjective rather as compliance against something which is not sufficiently defined is difficult.
2 | Assessment of Vulnerability Grades
2a | Categorisation of WwTW into Vulnerability Grades |  | The guidance for assessing 'Vulnerability Grades' for each catchment are set out in Appendix A of the "Developing and Trialling Wastewater Resilience Metrics - Final Report for Water UK (7 November 2017)". This guidance is very subjective and open to interpretation but we have developed a structured set of rules to ensure consistency of application across all catchments over 2,000PE as outlined in the methodology.
2b | Inclusion of catchments over 2,000PE |  | We used WwTW population PE to determine which catchments were over 2,000PE. There is no definition within the methodology to define PE and so as the metric relates to "population at risk" we have excluded PE associated with Trade flows.
2c | Inclusion of High and Medium Vulnerability Band catchments |  | We have reported population at risk in Vulnerability Grades 5, 4 & 3 as instructed by Ofwat. 'High' includes only grade 5 catchments, with 'Medium' including grade 4 & 3 catchments. 'Low' includes grades 2 & 1 and have been excluded from the calculation in accordance with the methodology.
2d | Use of 'Functional Areas' |  | The methodology allows companies the option to break larger catchments(over 4,000PE) into smaller 'Functional Areas' where there is good reason to indicate a catchment is be subject to different vulnerability (Page 21). As the HD catchments are small (Newtown is the largest at 12,000PE) we have not used 'Functional Areas' as the guidance on defining Vulnerability Bands is already subjectivity and splitting catchments into smaller areas is likely to add even more subjectivity.
3 | Modelling Population at Risk
3a | Modelling Approach |  | The methodology allows companies to choose whether to us the Buffered approach or the 2D overland flood routing approach set out in the methodology. We have chosen to use the simpler buffered approach as this is a simpler approach than using 2D modelling techniques. We have followed the methodology set out in Appendix C to ensure compliance.
3b | Determining Population at Risk |  | We have used AddressPoint property data to identify properties which fall within the flood risk buffers as per the methodology. We have then used catchment specific occupancy rates to convert properties to population.